Power Flame Incorporated

SUGGESTED SPECIFICATION

FOR

MODEL C(R) G HIGH TURNDOWN (HTD)

GAS BURNERS

THE POWER TO MANAGE ENERGY

2001 South 21st Street, Parsons, Kansas 67357

Telephone: 620-421-0480, Fax: 620-421-0948

Web Site: www.powerflame.com

E-Mail: CSD@ powerflame.com

| Copyright Power Flame Incorporated 1994 | C(R)GHTDSP1298 |
| --- | --- |

##### Suggested Specifications for Model C(R) G HTD

# Gas Burners

### Table of Contents

Section		Page(s)

General Burner Description	1

Approval Codes	1

Combustion Head Design	1

Ignition System	1

Burner Control Panel	1

Gas Train	2

Fuel/air Control System (Modulation)	2

Product Liability Insurance	2

Burner Start Up Information and Test Data	2-3

Suggested Specification for Model

C(R)G HIGH TURNDOWN (HTD) GAS BURNERS

(Note to specification writer - The below specification provides basic spec information for a typical U.L. code requirement.  We recommend that you refer to the PFI "Suggested Specification for Model CGO Combination Gas/Light Oil Burners" (CGOSP1294) for options and additional codes.

A.	GENERAL BURNER DESCRIPTION

- Furnish and install ________ Power Flame Model _________ forced draft High Turndown flame retention natural gas burners.  Each burner shall be capable of burning ______ CFH of ______ BTU/CU.FT Natural gas, with a specific gravity of _______.  Gas pressure supplied to the burner gas train supply connection shall be a minimum of ________ (in. W.C.) (PSIG) at full high rate and a maximum of _______ (in. W.C.) (PSIG) at static conditions.

- The burners will operate reliably with clean and stable combustion at a high fire to low fire turndown ratio of ______ to 1 and will comply with U.L. requirements.

B.	APPROVAL CODES

  - Each burner shall be listed by Underwriters Laboratories and shall bear the appropriate U.L.

label (in addition to the U.L. requirements, all equipment and installation procedures will meet the requirements of (IRI) (FM) (other)_____________ codes).  Each burner shall be designed and constructed as an integrated combustion system package and shall be factory fire tested.

C.	COMBUSTION HEAD DESIGN

- Each burner shall be of welded steel construction.  The combustion head shall incorporate

a multi blade, stainless steel, flame retention diffuser.  The gas firing head shall be of the multi-port type and constructed such as to place annular gas distribution opening between two parallel air flow streams to achieve maximum fuel/air mixing. The burner combustion head will carry full five (5) year replacement warranty.  Burners with cast alloy blower housings will not be accepted.

- (Spec writers - add the following for Scotch Marine boilers and/or very low gas pressure supply). The design shall also include a (fixed) (adjustable) primary air/gas mix chamber constructed such that a mixture of primary air and gas will be introduced into the combustion area, upstream of the secondary combustion air and ignition introduction zone. The burner combustion head will carry full five (5) year replacement warranty.

3.	All air required for combustion shall be supplied by a blower mounted integral to the burner.  The blower wheel shall be of the forward curved centrifugal design and shall be directly driven by a __________ HP 3450 RPM ________ volt, 60 Hertz _______ phase motor.  A dual blade damper assembly located on the inlet side of the blower wheel shall meter the combustion airflow.

D.	IGNITION SYSTEM

- The burner ignition system shall be natural gas.  The gas pilot system components shall include spark ignited pilot assembly, 6000 Volt ignition transformer, pilot solenoid valve, pilot gas pressure regulator and manual gas shutoff cock.  The flame proving system shall incorporate an Ultra-Violet flame detector, which will monitor both the pilot and main flames.  The pilot assembly shall fit within the confines of the blast tube - avoiding special burner front plate pilot cut outs.

1

E.	BURNER CONTROL PANEL

- All control components shall be mounted and wired within an integral burner mounted

control panel.  The panel shall incorporate an "Easy Access" (lift off) cover, and will include Power On and Main Fuel indicating lights and an On/Off control switch.

F.	GAS TRAIN (U.L.)

1.	The gas valve train shall contain the following:

a.	Manual Shutoff cock

b.	Main gas pressure regulator (Spec writer - Specify "tight shutoff type" if gas supply pressure exceeds 1 PSIG).

c.	Automatically operated main motorized gas valve (specify for inputs at 5.0 MBH and below).

- Automatically operated main motorized gas valve with proof of closure interlock switch (specify as standard above 5.0 MBTU/HR - option at or below 5.0 MBTU/HR).

e.	Automatically operated auxiliary gas valve.

f.	Manual reset Low and High Gas Pressure switches (specify as standard above 2500 MBH - option at 2500 MBH and below).

g.	Manual leak test cock.

h.	Burner manifold gas pressure gauge.

- Automatically operated Normally Open Vent Valve (specify as standard above 12,500

MBH), Optional at12,500 and below.

- FUEL/AIR CONTROL SYSTEM (MODULATION)

- The main On/Off gas supply shall be controlled by a motorized gas valve.  A modulating motor shall control the modulated positioning of the air inlet damper and butterfly type gas-proportioning valve to best meet varying system load conditions.

- The fuel/air control linkage between the modulating motor, air inlet control dampers and the gas butterfly valve shall employ the use of a quadrant linkage adjustment mechanism.  The quadrant design incorporates the use of adjustable high and low fire butterfly valve stops with a spring loaded over-travel mechanism for ease of linkage adjustment.

- A 135-Ohm or 4-20 milliamp, or 0-10 VDC, modulating type (temperature) (pressure) controller shall control the positioning of the modulating motor.  When the operating control is satisfied the burner shall shutoff and return to the low fire start position.  The modulating motor shall provide electrical interlock to insure a guaranteed low fire start position prior to the pilot trail for ignition sequence.

2

- PRODUCT LIABILITY INSURANCE

1.	The burner manufacturer will provide an insurance certificate documenting his current coverage of Product Liability Insurance with minimum coverage of $10,000,000.

I.	BURNER START UP INFORMATION AND TEST DATE

- On completion of the burner system start up - the installing contractor will complete the attached

"Burner Start Up and Test Data" form and deliver to the Specifying Engineer.

3

## BURNER START UP INFORMATION & TEST DATA

The following information shall be recorded for each burner start up:

| Power Flame Model |  | Invoice No. |  | Serial No. |  |
| --- | --- | --- | --- | --- | --- |

| Installation Name |  | Start Up Date |  |
| --- | --- | --- | --- |

| Start Up Contractors Name |  | Phone |  |
| --- | --- | --- | --- |

| Name of Technician doing Start Up |  |
| --- | --- |

| Type of Gas: | Nat. LP Other | Fuel Oil Grade No. |  |
| --- | --- | --- | --- |

| Gas Firing |
| --- |
| Gas Pressure at Train Inlet | Flame Signal Readings | Stack Outlet Test Draft |
| Burner in Off Position |  |  | Pilot |  | D.C. Volts | Low Fire |  | “ W.C. |
|  |  | Low Fire |  | D.C. Volts | High Fire |  | “ W.C. |
| Gas Pressure at Train Inlet | High Fire |  | D.C. Volts |  |
| Low Fire |  | “ W.C. |  |  | Net Stack Temperature |
| High Fire |  | “ W.C. | CO2 or O2 (Specify) | Low Fire |  | °F |
|  |  |  | Low Fire |  | % | High Fire |  | °F |
| Gas Pressure at Firing Head | High Fire |  | % |  |  |  |
| Low Fire |  | “ W.C. |  |  |  | Combustion Efficiency |
| High Fire |  | “ W.C. | CO |  | Low Fire |  | % |
|  |  |  | Low Fire |  | % | High Fire |  | % |
| Gas Pressure at Pilot Test Tee | High Fire |  | % |  |  |  |
|  | “ W.C. |  |  |  | Air Inlet Damper Opening High Fire |
|  |  |  | Input Rate BTU/HR |  | Top |  | in. |
| Power Supply | Low Fire |  |  | Bottom |  | in. |
| Volts |  | Ph |  | Hz |  |  | High Fire |  |  |  |  |  |
| Control Circuit Volts |  |  |  |  |  |  |  |  |
| Blower Motor amps at high fire |  | Over Fire Draft |  |  |  |  |
|  |  | Low Fire |  | “ W.C. |  |  |  |
|  |  |  | High Fire |  | “ W.C. |  |  |  |
| Control Settings |
| General |  |  |
| Operating control cut out setting | Limit control cut out setting | Low gas pressure switch |  | in. |
|  |  |  |  | High gas pressure switch |  | in. |
|  |  |  | Limit control cut in setting |  |
| Operating control cut in setting |  |  |  |  |  |  |
| Operation Checklist |
| Checked For Proper Operation Of: |  | Yes |  | No |  |  | Yes |  | No |
| Low water cut off |  |  |  |  |  | Barometric damper |  |  |  |
| High water cut off |  |  |  |  |  | Boiler room combustion air & |  |  |  |
| Flame safeguard control ignition failure |  |  |  |  |  | ventilation provision correct |  |  |  |
| Flame safeguard control main flame failure |  |  |  |  |  | Oil tank vent system correct |  |  |  |
| Burner air flow switch |  |  |  |  |  | All oil lines checked for leaks |  |  |  |
| Induced draft fan controls |  |  |  |  |  | All gas lines checked for leaks |  |  |  |
| Over fire draft controls |  |  |  |  |  | Gas lines & controls properly vented |  |  |  |
| Fresh air damper end switch |  |  |  |  |  | Other system components (specify) |  |  |  |

| Notified |  | of the following system deficiencies: |  |
| --- | --- | --- | --- |

4