Power Flame Incorporated

SUGGESTED SPECIFICATION

FOR MODEL

NPM

LOW NOx

GAS BURNERS

SUB 30 PPM NOx

THE POWER TO MANAGE ENERGY

2001 South 21st Street, Parsons, Kansas 67357

Telephone: 620-421-0480, Fax: 620-421-0948

Web Site: www.powerflame.com

E-Mail: CSD@ powerflame.com

| Copyright Power Flame Incorporated 2003 | NPMSP0803 |
| --- | --- |
|  | Rev. 0406 |

##### Suggested Specifications for Model NPM

# Low NOx Gas Burners

### Table of Contents

Section		Page(s)

General Burner Description	1

Burner Control Panel	1

Fuel air control	1-2

Emission requirements 	2

Product Liability Insurance	2

Burner Start Up Information and Test Data	3

Suggested Specification for Model

### NPM LOW NOx GAS BURNERS

#### GENERAL BURNER DESCRIPTION

Furnish and install ___________ Power Flame Model __________ forced draft, fully premixed, flame retention (natural gas) or (propane gas) burners.  Each burner shall be capable of burning _____ CFH of _______ BTU/CU.FT. (natural gas) or (propane gas), with a specific gravity of _______.  Gas pressure supplied to the burner gas train supply connection shall be a minimum of _______ (In. w.c.) (PSIG) at full high rate and a maximum of _______ (In. w.c.) (PSIG) at static conditions.

Each burner shall be listed by Underwriters laboratories and shall bear the appropriate UL label.  (In addition to the UL requirements, all equipment and installation procedures will meet the requirements of (IRI), (FM), (Other) _______ codes).  Each burner shall be designed and constructed as an integrated combustion system package - and shall be factory fire tested.

Each burner shall be of welded steel construction and have a baked on powder coat finish. The firing head shall be of the full premix design and incorporate a stainless steel high swirl stabilized combustion flame retention diffusor.  Mixing of the fuel and air must take place on the discharge side of the blower wheel to insure safe combustion. Units that mix fuel and air prior to the blower inlet will not be accepted.  The integral blower assembly will supply all the required air for combustion. The blower wheel shall be of a forward curved “Squirrel Cage” design and shall be directly driven by a _______HP, 3450 RPM _______ Volt, 60 Hertz _______ phase motor.  A combustion air damper assembly shall meter the combustion airflow.

The burner ignition system shall be (natural gas) or (propane gas).  The pilot system components shall include spark ignited pilot assembly, 6000 Volt ignition transformer, pilot solenoid valve, pilot pressure regulator and manual gas shutoff cock.  The flame proving system shall incorporate a flame rod sensor.

#### BURNER CONTROL PANEL

All control components shall be mounted and wired within an integral burner mounted control panel.  The panel shall incorporate a Main Fuel indicating light and an On/Off control switch.

### Fuel/Air Control System

(Spec writer - select one of the following described systems 1 through 4).

1.	On-Off Gas

The main gas supply shall be controlled by a SELECT ONE (single valve body with dual shutoff gas valves and regulator) or (motorized main gas valve, combination auxiliary solenoid valve and gas regulator) or (single motorized gas valve with proof of closure, separate gas regulator) The air inlet control dampers shall be fixed at the optimum fuel/air ratio at the high fire position.

2.	Low-High-Off Gas

The main gas supply shall be controlled by a motorized gas valve mechanically linked to air inlet control dampers which will provide a reduced fuel/air volume for low fire start and then mechanically open to the high fire run position. SELECT ONE (auxiliary solenoid gas valve) or (combination auxiliary diaphragm gas valve and gas regulator) or (provide main motorized gas valve with proof of closure switch and separate gas regulator). When the operating control is satisfied the burner will shutoff and return to the low fire start position.

1

3.	Low-High-Low Gas

The main gas on-off supply shall be controlled by a SELECT ONE (motorized main gas valve, auxiliary solenoid valve and separate gas regulator) or (single motorized gas valve with proof of closure and separate gas regulator). Direct drive motor mechanically linked to the air inlet control damper will provide a reduced air volume for low fire start and then mechanically open to the high fire run position. Butterfly type gas proportioning valve will control the fuel supply between the low and high fire positions.

A Low-High-Low, two position, (temperature) (pressure) control shall electrically switch the burner to low or high fire position to best meet varying system load conditions.  When the operating control is satisfied the burner shall shutoff and return to the low fire start position.

4.	Modulation

The main On-Off gas supply shall be controlled by a SELECT ONE (single valve body with dual shutoff gas valves and regulator) or (motorized main gas valve, combination auxiliary solenoid valve and gas regulator) or (single motorized gas valve with proof of closure, separate gas regulator) A modulating motor shall control the modulated positioning of the air inlet dampers, butterfly type gas proportioning valve to best meet varying system load conditions.

The positioning of the modulating motor shall be controlled by (135 Ohm), (4-20 mA), (0-10 VDC) modulating type (temperature), (pressure) controller.  When the operating control is satisfied the burner will shutoff and return to the low fire start position.  The modulating motor shall provide electrical interlock to insure a guaranteed low fire start position prior to the pilot trial for ignition sequence

EMISSIONS REQUIREMENTS

The burner will produce less than 30 parts per million NOx and less than 50 parts per million CO without the use of flue gas recirculation. The burner will operate with uniform heat flux and flame stability. Burners requiring flue gas recirculation will not be accepted.

#### PRODUCT LIABILITY INSURANCE

The burner manufacturer will provide an insurance certificate documenting his current coverage of Product Liability Insurance with minimum coverage of $10,000,000.

#### BURNER START UP INFORMATION AND TEST DATA

On completion of the burner system start up - the installing contractor will complete the attached “Burner Start Up and Test Data” form and deliver to the Specifying Engineer.

2

## BURNER START UP INFORMATION & TEST DATA

The following information shall be recorded for each burner start up:

| Power Flame Model |  | Invoice No. |  | Serial No. |  |
| --- | --- | --- | --- | --- | --- |

| Installation Name |  | Start Up Date |  |
| --- | --- | --- | --- |

| Start Up Contractors Name |  | Phone |  |
| --- | --- | --- | --- |

| Name of Technician doing Start Up |  |
| --- | --- |

| Type of Gas: | Nat. LP Other |  |
| --- | --- | --- |

| Gas Firing |
| --- |
| Gas Pressure at Train Inlet | Flame Signal Readings | Stack Outlet Test Draft |
| Burner in Off Position |  |  | Pilot |  | D.C. Volts | Low Fire |  | “ W.C. |
|  |  | Low Fire |  | D.C. Volts | High Fire |  | “ W.C. |
| Gas Pressure at Train Inlet | High Fire |  | D.C. Volts |  |
| Low Fire |  | “ W.C. |  |  | Net Stack Temperature |
| High Fire |  | “ W.C. | CO2 or O2 (Specify) | Low Fire |  | °F |
|  |  |  | Low Fire |  | % | High Fire |  | °F |
| Gas Pressure at Firing Head | High Fire |  | % |  |  |  |
| Low Fire |  | “ W.C. |  |  |  | Combustion Efficiency |
| High Fire |  | “ W.C. | CO |  | Low Fire |  | % |
|  |  |  | Low Fire |  | % | High Fire |  | % |
| Gas Pressure at Pilot Test Tee | High Fire |  | % |  |  |  |
|  | “ W.C. |  |  |  | Air Inlet Damper Opening High Fire |
|  |  |  | Input Rate BTU/HR |  | Top |  | in. |
| Power Supply | Low Fire |  |  | Bottom |  | in. |
| Volts |  | Ph |  | Hz |  |  | High Fire |  |  |  |  |  |
| Control Circuit Volts |  |  |  |  |  |  |  |  |
| Blower Motor amps at high fire |  | Over Fire Draft |  |  |  |  |
|  |  | Low Fire |  | “ W.C. |  |  |  |
|  |  |  | High Fire |  | “ W.C. |  |  |  |
| Control Settings |
| General |  |  |
| Operating control cut out setting | Limit control cut out setting | Low gas pressure switch |  | in. |
|  |  |  |  | High gas pressure switch |  | in. |
| Operating control cut in setting | Limit control cut in setting |  |
| Operation Checklist |
| Checked For Proper Operation Of: |  | Yes |  | No |  |  | Yes |  | No |
| Low water cut off |  |  |  |  |  | Barometric damper |  |  |  |
| High water cut off |  |  |  |  |  | Boiler room combustion air & |  |  |  |
| Flame safeguard control ignition failure |  |  |  |  |  | ventilation provision correct |  |  |  |
| Flame safeguard control main flame failure |  |  |  |  |  |  |  |  |  |
| Burner air flow switch |  |  |  |  |  |  |  |  |  |
| Induced draft fan controls |  |  |  |  |  | All gas lines checked for leaks |  |  |  |
| Over fire draft controls |  |  |  |  |  | Gas lines & controls properly vented |  |  |  |
| Fresh air damper end switch |  |  |  |  |  | Other system components (specify) |  |  |  |

| Notified |  | of the following system deficiencies: |  |
| --- | --- | --- | --- |

3